## VDAS Data
Time | MFP100 1.5kW Motor Drive |  |  | DP3 Digital Pressure Display |  |  |  | Analogue Input Board |  |  |  | Calculated Parameters | [5 empty] | Test Conditions |  |  |  |  | Nozzle Parameters
Time | Speed | Torque | Power | D P1 | P2 | P3 | P4 [Absolute] | Voltage 1 | Current 1 | Voltage 2 | Current 2 | Mass Flow Rate | Volumetric Flow Rate | Fan Total Pressure | Air Power | Fan Efficiency | Specific Speed | Configuration | Impeller | Ambient Temperature | Slide Valve Position | Mechanical Power Loss | Nozzle Diameter | Nozzle Area | Nozzle Discharge Coefficient
(s) | (rev.min-1) | (Nm) | (W) | (Pa) | (Pa) | (Pa) | (mbar) | (V) | (mA) | (V) | (mA) | (kg.s-1) | (m3.s-1) | (Pa) | (W) | (%) | (rev.min-1) |  |  | (°C) | (%) | (W) | (m) | (m2)
Data Series 1
0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1500 | 0.27 | 43 | -364 | -219 | 36 | 1009 | 0 | 0 | 0 | 0 | 0.1244 | 0.1044 | 255 | 27 | 71.1 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
1 | 1500 | 0.28 | 44 | -364 | -219 | 36 | 1009 | 0 | 0 | 0 | 0 | 0.1244 | 0.1044 | 255 | 27 | 69.2 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1500 | 0.28 | 44 | -364 | -217 | 36 | 1009 | 0 | 0 | 0 | 0 | 0.1244 | 0.1044 | 253 | 26 | 66.7 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
2 | 1500 | 0.28 | 44 | -364 | -217 | 36 | 1009 | 0 | 0 | 0 | 0 | 0.1244 | 0.1044 | 253 | 26 | 66.7 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1500 | 0.28 | 44 | -364 | -218 | 36 | 1009 | 0 | 0 | 0 | 0 | 0.1244 | 0.1044 | 254 | 27 | 69.2 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
3 | 1500 | 0.28 | 44 | -364 | -218 | 37 | 1009 | 0 | 0 | 0 | 0 | 0.1244 | 0.1044 | 255 | 27 | 69.2 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1500 | 0.27 | 43 | -362 | -217 | 37 | 1009 | 0 | 0 | 0 | 0 | 0.1241 | 0.1042 | 254 | 26 | 68.4 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
4 | 1500 | 0.27 | 43 | -362 | -217 | 36 | 1009 | 0 | 0 | 0 | 0 | 0.1241 | 0.1042 | 253 | 26 | 68.4 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1500 | 0.28 | 44 | -358 | -217 | 36 | 1009 | 0 | 0 | 0 | 0 | 0.1234 | 0.1036 | 253 | 26 | 66.7 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
5 | 1500 | 0.28 | 44 | -358 | -217 | 37 | 1009 | 0 | 0 | 0 | 0 | 0.1234 | 0.1036 | 254 | 26 | 66.7 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
Data Series 2
0 | 1983 | 0.28 | 59 | -360 | -217 | 39 | 1009 | 0 | 0 | 0 | 0 | 0.1237 | 0.1038 | 256 | 27 | 50 | 55 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1809 | 0.28 | 54 | -364 | -216 | 38 | 1009 | 0 | 0 | 0 | 0 | 0.1244 | 0.1044 | 254 | 27 | 55.1 | 51 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
1 | 1747 | 0.28 | 52 | -366 | -216 | 38 | 1009 | 0 | 0 | 0 | 0 | 0.1247 | 0.1047 | 254 | 27 | 57.4 | 49 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1697 | 0.28 | 50 | -366 | -218 | 38 | 1009 | 0 | 0 | 0 | 0 | 0.1247 | 0.1047 | 256 | 27 | 60 | 48 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
2 | 1627 | 0.28 | 48 | -366 | -218 | 38 | 1009 | 0 | 0 | 0 | 0 | 0.1247 | 0.1047 | 256 | 27 | 62.8 | 46 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1601 | 0.28 | 47 | -362 | -214 | 38 | 1009 | 0 | 0 | 0 | 0 | 0.1241 | 0.1042 | 252 | 26 | 61.9 | 45 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
3 | 1581 | 0.28 | 47 | -362 | -214 | 38 | 1009 | 0 | 0 | 0 | 0 | 0.1241 | 0.1042 | 252 | 26 | 61.9 | 45 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1552 | 0.28 | 46 | -366 | -213 | 38 | 1009 | 0 | 0 | 0 | 0 | 0.1247 | 0.1047 | 251 | 26 | 63.4 | 44 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
4 | 1542 | 0.28 | 46 | -366 | -213 | 38 | 1009 | 0 | 0 | 0 | 0 | 0.1247 | 0.1047 | 251 | 26 | 63.4 | 44 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1534 | 0.27 | 44 | -362 | -213 | 38 | 1009 | 0 | 0 | 0 | 0 | 0.1241 | 0.1042 | 251 | 26 | 66.7 | 43 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
5 | 1522 | 0.27 | 43 | -362 | -216 | 39 | 1009 | 0 | 0 | 0 | 0 | 0.1241 | 0.1042 | 255 | 27 | 71.1 | 43 | Fan Tests | Backward Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
Data Series 3
0 | 1502 | 0.27 | 43 | -336 | -200 | 57 | 1009 | 0 | 0 | 0 | 0 | 0.1195 | 0.1003 | 257 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1502 | 0.27 | 43 | -336 | -200 | 58 | 1009 | 0 | 0 | 0 | 0 | 0.1195 | 0.1003 | 258 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
1 | 1502 | 0.27 | 43 | -338 | -200 | 58 | 1009 | 0 | 0 | 0 | 0 | 0.1199 | 0.1006 | 258 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.27 | 43 | -338 | -199 | 57 | 1009 | 0 | 0 | 0 | 0 | 0.1199 | 0.1006 | 256 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.27 | 43 | -334 | -199 | 57 | 1009 | 0 | 0 | 0 | 0 | 0.1192 | 0.1001 | 256 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.27 | 43 | -334 | -200 | 57 | 1009 | 0 | 0 | 0 | 0 | 0.1192 | 0.1001 | 257 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.27 | 43 | -334 | -200 | 57 | 1009 | 0 | 0 | 0 | 0 | 0.1192 | 0.1001 | 257 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.27 | 43 | -332 | -203 | 57 | 1009 | 0 | 0 | 0 | 0 | 0.1188 | 0.0997 | 260 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.27 | 43 | -332 | -203 | 57 | 1009 | 0 | 0 | 0 | 0 | 0.1188 | 0.0997 | 260 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.27 | 43 | -336 | -202 | 57 | 1009 | 0 | 0 | 0 | 0 | 0.1195 | 0.1003 | 259 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.27 | 43 | -336 | -202 | 57 | 1009 | 0 | 0 | 0 | 0 | 0.1195 | 0.1003 | 259 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
5.5 | 1501 | 0.27 | 43 | -334 | -202 | 57 | 1009 | 0 | 0 | 0 | 0 | 0.1192 | 0.1001 | 259 | 26 | 68.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
Data Series 4
0 | 1501 | 0.27 | 43 | -298 | -171 | 80 | 1009 | 0 | 0 | 0 | 0 | 0.1126 | 0.0945 | 251 | 24 | 63.2 | 41 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1501 | 0.27 | 43 | -298 | -179 | 80 | 1009 | 0 | 0 | 0 | 0 | 0.1126 | 0.0945 | 259 | 24 | 63.2 | 40 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
1 | 1501 | 0.27 | 43 | -298 | -179 | 80 | 1009 | 0 | 0 | 0 | 0 | 0.1126 | 0.0945 | 259 | 24 | 63.2 | 40 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.27 | 43 | -300 | -180 | 80 | 1009 | 0 | 0 | 0 | 0 | 0.1129 | 0.0948 | 260 | 25 | 65.8 | 40 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.27 | 43 | -300 | -180 | 80 | 1009 | 0 | 0 | 0 | 0 | 0.1129 | 0.0948 | 260 | 25 | 65.8 | 40 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.27 | 43 | -298 | -179 | 80 | 1009 | 0 | 0 | 0 | 0 | 0.1126 | 0.0945 | 259 | 24 | 63.2 | 40 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.27 | 43 | -298 | -179 | 79 | 1009 | 0 | 0 | 0 | 0 | 0.1126 | 0.0945 | 258 | 24 | 63.2 | 40 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.27 | 43 | -294 | -179 | 79 | 1009 | 0 | 0 | 0 | 0 | 0.1118 | 0.0938 | 258 | 24 | 63.2 | 40 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.27 | 43 | -294 | -179 | 81 | 1009 | 0 | 0 | 0 | 0 | 0.1118 | 0.0938 | 260 | 24 | 63.2 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.27 | 43 | -296 | -179 | 81 | 1009 | 0 | 0 | 0 | 0 | 0.1122 | 0.0942 | 260 | 24 | 63.2 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.27 | 43 | -296 | -181 | 81 | 1009 | 0 | 0 | 0 | 0 | 0.1122 | 0.0942 | 262 | 25 | 65.8 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
Data Series 5
0 | 1501 | 0.26 | 41 | -240 | -149 | 113 | 1009 | 0 | 0 | 0 | 0 | 0.101 | 0.0848 | 262 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1501 | 0.26 | 41 | -240 | -149 | 113 | 1009 | 0 | 0 | 0 | 0 | 0.101 | 0.0848 | 262 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
1 | 1501 | 0.26 | 41 | -240 | -146 | 113 | 1009 | 0 | 0 | 0 | 0 | 0.101 | 0.0848 | 259 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.26 | 41 | -240 | -146 | 114 | 1009 | 0 | 0 | 0 | 0 | 0.101 | 0.0848 | 260 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.26 | 41 | -240 | -148 | 114 | 1009 | 0 | 0 | 0 | 0 | 0.101 | 0.0848 | 262 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.26 | 41 | -240 | -148 | 113 | 1009 | 0 | 0 | 0 | 0 | 0.101 | 0.0848 | 261 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.26 | 41 | -238 | -148 | 113 | 1009 | 0 | 0 | 0 | 0 | 0.1006 | 0.0844 | 261 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.26 | 41 | -238 | -148 | 114 | 1009 | 0 | 0 | 0 | 0 | 0.1006 | 0.0844 | 262 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.26 | 41 | -240 | -148 | 114 | 1009 | 0 | 0 | 0 | 0 | 0.101 | 0.0848 | 262 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.26 | 41 | -240 | -147 | 114 | 1009 | 0 | 0 | 0 | 0 | 0.101 | 0.0848 | 261 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.26 | 41 | -240 | -147 | 114 | 1009 | 0 | 0 | 0 | 0 | 0.101 | 0.0848 | 261 | 22 | 61.1 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
Data Series 6
0 | 1501 | 0.25 | 40 | -176 | -104 | 154 | 1009 | 0 | 0 | 0 | 0 | 0.0865 | 0.0726 | 258 | 19 | 54.3 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1501 | 0.25 | 40 | -176 | -113 | 148 | 1009 | 0 | 0 | 0 | 0 | 0.0865 | 0.0726 | 261 | 19 | 54.3 | 34 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
1 | 1501 | 0.25 | 40 | -180 | -113 | 148 | 1009 | 0 | 0 | 0 | 0 | 0.0875 | 0.0734 | 261 | 19 | 54.3 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.25 | 40 | -180 | -112 | 147 | 1009 | 0 | 0 | 0 | 0 | 0.0875 | 0.0734 | 259 | 19 | 54.3 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.25 | 40 | -180 | -112 | 147 | 1009 | 0 | 0 | 0 | 0 | 0.0875 | 0.0734 | 259 | 19 | 54.3 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.25 | 40 | -178 | -115 | 147 | 1009 | 0 | 0 | 0 | 0 | 0.087 | 0.073 | 262 | 19 | 54.3 | 34 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.25 | 40 | -178 | -115 | 147 | 1009 | 0 | 0 | 0 | 0 | 0.087 | 0.073 | 262 | 19 | 54.3 | 34 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.25 | 40 | -178 | -112 | 147 | 1009 | 0 | 0 | 0 | 0 | 0.087 | 0.073 | 259 | 19 | 54.3 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.25 | 40 | -178 | -112 | 147 | 1009 | 0 | 0 | 0 | 0 | 0.087 | 0.073 | 259 | 19 | 54.3 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.25 | 40 | -180 | -112 | 147 | 1009 | 0 | 0 | 0 | 0 | 0.0875 | 0.0734 | 259 | 19 | 54.3 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.25 | 40 | -180 | -111 | 147 | 1009 | 0 | 0 | 0 | 0 | 0.0875 | 0.0734 | 258 | 19 | 54.3 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
Data Series 7
0 | 1501 | 0.24 | 39 | -110 | -73 | 182 | 1009 | 0 | 0 | 0 | 0 | 0.0684 | 0.0574 | 255 | 15 | 44.1 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1501 | 0.24 | 39 | -110 | -73 | 182 | 1009 | 0 | 0 | 0 | 0 | 0.0684 | 0.0574 | 255 | 15 | 44.1 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
1 | 1501 | 0.24 | 39 | -110 | -74 | 183 | 1009 | 0 | 0 | 0 | 0 | 0.0684 | 0.0574 | 257 | 15 | 44.1 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.24 | 39 | -110 | -74 | 183 | 1009 | 0 | 0 | 0 | 0 | 0.0684 | 0.0574 | 257 | 15 | 44.1 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.24 | 39 | -110 | -74 | 182 | 1009 | 0 | 0 | 0 | 0 | 0.0684 | 0.0574 | 256 | 15 | 44.1 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.24 | 39 | -108 | -74 | 182 | 1009 | 0 | 0 | 0 | 0 | 0.0678 | 0.0569 | 256 | 15 | 44.1 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.24 | 39 | -108 | -72 | 182 | 1009 | 0 | 0 | 0 | 0 | 0.0678 | 0.0569 | 254 | 14 | 41.2 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.23 | 37 | -108 | -72 | 183 | 1009 | 0 | 0 | 0 | 0 | 0.0678 | 0.0569 | 255 | 15 | 46.9 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.23 | 37 | -108 | -72 | 183 | 1009 | 0 | 0 | 0 | 0 | 0.0678 | 0.0569 | 255 | 15 | 46.9 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.24 | 39 | -108 | -72 | 184 | 1009 | 0 | 0 | 0 | 0 | 0.0678 | 0.0569 | 256 | 15 | 44.1 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.24 | 39 | -108 | -74 | 184 | 1009 | 0 | 0 | 0 | 0 | 0.0678 | 0.0569 | 258 | 15 | 44.1 | 31 | Fan Tests | Backward Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
Data Series 8
0 | 1501 | 0.22 | 36 | -56 | -39 | 206 | 1009 | 0 | 0 | 0 | 0 | 0.0488 | 0.041 | 245 | 10 | 32.3 | 27 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1501 | 0.22 | 36 | -56 | -39 | 205 | 1009 | 0 | 0 | 0 | 0 | 0.0488 | 0.041 | 244 | 10 | 32.3 | 27 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
1 | 1501 | 0.22 | 36 | -68 | -47 | 205 | 1009 | 0 | 0 | 0 | 0 | 0.0538 | 0.0452 | 252 | 11 | 35.5 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.22 | 36 | -68 | -47 | 201 | 1009 | 0 | 0 | 0 | 0 | 0.0538 | 0.0452 | 248 | 11 | 35.5 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.22 | 36 | -66 | -47 | 201 | 1009 | 0 | 0 | 0 | 0 | 0.053 | 0.0445 | 248 | 11 | 35.5 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.22 | 36 | -66 | -46 | 201 | 1009 | 0 | 0 | 0 | 0 | 0.053 | 0.0445 | 247 | 11 | 35.5 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.22 | 36 | -66 | -46 | 201 | 1009 | 0 | 0 | 0 | 0 | 0.053 | 0.0445 | 247 | 11 | 35.5 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.22 | 36 | -66 | -47 | 201 | 1009 | 0 | 0 | 0 | 0 | 0.053 | 0.0445 | 248 | 11 | 35.5 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.22 | 36 | -66 | -47 | 201 | 1009 | 0 | 0 | 0 | 0 | 0.053 | 0.0445 | 248 | 11 | 35.5 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.22 | 36 | -68 | -46 | 201 | 1009 | 0 | 0 | 0 | 0 | 0.0538 | 0.0452 | 247 | 11 | 35.5 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.22 | 36 | -68 | -46 | 202 | 1009 | 0 | 0 | 0 | 0 | 0.0538 | 0.0452 | 248 | 11 | 35.5 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
Data Series 9
0 | 1501 | 0.21 | 33 | -30 | -21 | 211 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 232 | 7 | 25 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1501 | 0.21 | 33 | -30 | -21 | 211 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 232 | 7 | 25 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
1 | 1501 | 0.2 | 31 | -30 | -21 | 212 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 233 | 7 | 26.9 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.21 | 33 | -30 | -21 | 212 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 233 | 7 | 25 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.2 | 31 | -30 | -21 | 212 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 233 | 7 | 26.9 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.2 | 31 | -30 | -21 | 212 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 233 | 7 | 26.9 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.2 | 31 | -30 | -22 | 212 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 234 | 7 | 26.9 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.2 | 31 | -30 | -22 | 212 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 234 | 7 | 26.9 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.2 | 31 | -30 | -21 | 212 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 233 | 7 | 26.9 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.2 | 31 | -30 | -21 | 214 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 235 | 7 | 26.9 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.21 | 33 | -30 | -21 | 214 | 1009 | 0 | 0 | 0 | 0 | 0.0357 | 0.03 | 235 | 7 | 25 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
Data Series 10
0 | 1501 | 0.18 | 28 | -6 | -6 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.016 | 0.0134 | 223 | 3 | 13 | 17 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1501 | 0.19 | 30 | -8 | -6 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.0184 | 0.0154 | 223 | 3 | 12 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
1 | 1501 | 0.19 | 30 | -8 | -6 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.0184 | 0.0154 | 223 | 3 | 12 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.19 | 30 | -8 | -6 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.0184 | 0.0154 | 223 | 3 | 12 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.19 | 30 | -6 | -6 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.016 | 0.0134 | 223 | 3 | 12 | 17 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.19 | 30 | -6 | -6 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.016 | 0.0134 | 223 | 3 | 12 | 17 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.18 | 28 | -6 | -7 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.016 | 0.0134 | 224 | 3 | 13 | 17 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.18 | 28 | -6 | -7 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.016 | 0.0134 | 224 | 3 | 13 | 17 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.19 | 30 | -6 | -7 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.016 | 0.0134 | 224 | 3 | 12 | 17 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.19 | 30 | -6 | -6 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.016 | 0.0134 | 223 | 3 | 12 | 17 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.19 | 30 | -6 | -6 | 217 | 1009 | 0 | 0 | 0 | 0 | 0.016 | 0.0134 | 223 | 3 | 12 | 17 | Fan Tests | Backward Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
Data Series 11
0 | 1501 | 0.17 | 27 | 0 | 10 | 228 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1501 | 0.17 | 27 | 0 | 10 | 228 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
1 | 1501 | 0.17 | 27 | 0 | 9 | 229 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.17 | 27 | 0 | 9 | 229 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.17 | 27 | 0 | 9 | 228 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.17 | 27 | 0 | 9 | 228 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.17 | 27 | 0 | 9 | 228 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.17 | 27 | 0 | 9 | 229 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.17 | 27 | 0 | 9 | 229 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.17 | 27 | 0 | 9 | 229 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.17 | 27 | 0 | 10 | 229 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96