## VDAS Data
Time | MFP100 1.5kW Motor Drive |  |  | DP3 Digital Pressure Display |  |  |  | Analogue Input Board |  |  |  | Calculated Parameters | [5 empty] | Test Conditions |  |  |  |  | Nozzle Parameters
Time | Speed | Torque | Power | D P1 | P2 | P3 | P4 [Absolute] | Voltage 1 | Current 1 | Voltage 2 | Current 2 | Mass Flow Rate | Volumetric Flow Rate | Fan Total Pressure | Air Power | Fan Efficiency | Specific Speed | Configuration | Impeller | Ambient Temperature | Slide Valve Position | Mechanical Power Loss | Nozzle Diameter | Nozzle Area | Nozzle Discharge Coefficient
(s) | (rev.min-1) | (Nm) | (W) | (Pa) | (Pa) | (Pa) | (mbar) | (V) | (mA) | (V) | (mA) | (kg.s-1) | (m3.s-1) | (Pa) | (W) | (%) | (rev.min-1) |  |  | (°C) | (%) | (W) | (m) | (m2)
Data Series 1
0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3005 | 0.75 | 237 | -1548 | -873 | 151 | 1009 | 0 | 0 | 0 | 0 | 0.2565 | 0.2153 | 1024 | 220 | 98.7 | 43 | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
1 | 3005 | 0.75 | 237 | -1520 | -873 | 151 | 1009 | 0 | 0 | 0 | 0 | 0.2542 | 0.2134 | 1024 | 219 | 98.2 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3005 | 0.75 | 237 | -1520 | -873 | 151 | 1009 | 0 | 0 | 0 | 0 | 0.2542 | 0.2134 | 1024 | 219 | 98.2 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
2 | 3005 | 0.75 | 237 | -1448 | -873 | 151 | 1009 | 0 | 0 | 0 | 0 | 0.2481 | 0.2083 | 1024 | 213 | 95.5 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3005 | 0.75 | 237 | -1448 | -874 | 151 | 1009 | 0 | 0 | 0 | 0 | 0.2481 | 0.2083 | 1025 | 214 | 96 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
3 | 3005 | 0.75 | 237 | -1494 | -874 | 151 | 1009 | 0 | 0 | 0 | 0 | 0.252 | 0.2115 | 1025 | 217 | 97.3 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3005 | 0.75 | 237 | -1494 | -871 | 150 | 1009 | 0 | 0 | 0 | 0 | 0.252 | 0.2115 | 1021 | 216 | 96.9 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
4 | 3005 | 0.75 | 237 | -1494 | -871 | 150 | 1009 | 0 | 0 | 0 | 0 | 0.252 | 0.2115 | 1021 | 216 | 96.9 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3005 | 0.75 | 237 | -1494 | -868 | 150 | 1009 | 0 | 0 | 0 | 0 | 0.252 | 0.2115 | 1018 | 215 | 96.4 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
5 | 3005 | 0.75 | 237 | -1494 | -868 | 151 | 1009 | 0 | 0 | 0 | 0 | 0.252 | 0.2115 | 1019 | 216 | 96.9 | 42 | Fan Tests | Backward Swept | 22.1 | 100 | 14 | 0.075 | 0.0044 | 0.96
Data Series 2
0 | 3005 | 0.75 | 237 | -1500 | -864 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2525 | 0.2119 | 1027 | 218 | 97.8 | 42 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3005 | 0.75 | 237 | -1500 | -864 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2525 | 0.2119 | 1027 | 218 | 97.8 | 42 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
1 | 3005 | 0.75 | 237 | -1474 | -864 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2503 | 0.2101 | 1027 | 216 | 96.9 | 42 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3005 | 0.75 | 237 | -1474 | -855 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2503 | 0.2101 | 1018 | 214 | 96 | 42 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
2 | 3005 | 0.75 | 237 | -1500 | -855 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2525 | 0.2119 | 1018 | 216 | 96.9 | 43 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3005 | 0.75 | 237 | -1500 | -857 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2525 | 0.2119 | 1020 | 216 | 96.9 | 42 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
3 | 3005 | 0.75 | 237 | -1476 | -857 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2505 | 0.2103 | 1020 | 215 | 96.4 | 42 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3005 | 0.75 | 237 | -1476 | -870 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2505 | 0.2103 | 1033 | 217 | 97.3 | 42 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
4 | 3005 | 0.75 | 237 | -1476 | -870 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2505 | 0.2103 | 1033 | 217 | 97.3 | 42 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3005 | 0.75 | 237 | -1472 | -869 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2502 | 0.21 | 1032 | 217 | 97.3 | 42 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
5 | 3005 | 0.75 | 237 | -1472 | -869 | 163 | 1009 | 0 | 0 | 0 | 0 | 0.2502 | 0.21 | 1032 | 217 | 97.3 | 42 | Fan Tests | Backward Swept | 22.1 | 90 | 14 | 0.075 | 0.0044 | 0.96
Data Series 3
0 | 3005 | 0.74 | 234 | -1380 | -781 | 255 | 1009 | 0 | 0 | 0 | 0 | 0.2422 | 0.2033 | 1036 | 211 | 95.9 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3005 | 0.74 | 234 | -1380 | -776 | 255 | 1009 | 0 | 0 | 0 | 0 | 0.2422 | 0.2033 | 1031 | 210 | 95.5 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
1 | 3005 | 0.74 | 234 | -1390 | -776 | 255 | 1009 | 0 | 0 | 0 | 0 | 0.2431 | 0.2041 | 1031 | 210 | 95.5 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3005 | 0.74 | 234 | -1390 | -791 | 256 | 1009 | 0 | 0 | 0 | 0 | 0.2431 | 0.2041 | 1047 | 214 | 97.3 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
2 | 3005 | 0.73 | 231 | -1388 | -791 | 256 | 1009 | 0 | 0 | 0 | 0 | 0.2429 | 0.2039 | 1047 | 213 | 98.2 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3005 | 0.74 | 234 | -1388 | -784 | 256 | 1009 | 0 | 0 | 0 | 0 | 0.2429 | 0.2039 | 1040 | 212 | 96.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
3 | 3005 | 0.74 | 234 | -1388 | -784 | 255 | 1009 | 0 | 0 | 0 | 0 | 0.2429 | 0.2039 | 1039 | 212 | 96.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3005 | 0.74 | 234 | -1290 | -789 | 255 | 1009 | 0 | 0 | 0 | 0 | 0.2342 | 0.1966 | 1044 | 205 | 93.2 | 40 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
4 | 3005 | 0.74 | 234 | -1290 | -789 | 255 | 1009 | 0 | 0 | 0 | 0 | 0.2342 | 0.1966 | 1044 | 205 | 93.2 | 40 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3005 | 0.74 | 234 | -1378 | -789 | 255 | 1009 | 0 | 0 | 0 | 0 | 0.242 | 0.2031 | 1044 | 212 | 96.4 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
5 | 3005 | 0.74 | 234 | -1378 | -786 | 255 | 1009 | 0 | 0 | 0 | 0 | 0.242 | 0.2031 | 1041 | 211 | 95.9 | 41 | Fan Tests | Backward Swept | 22.1 | 80 | 14 | 0.075 | 0.0044 | 0.96
Data Series 4
0 | 3005 | 0.73 | 231 | -1192 | -700 | 351 | 1009 | 0 | 0 | 0 | 0 | 0.2251 | 0.1889 | 1051 | 199 | 91.7 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3005 | 0.72 | 228 | -1192 | -700 | 352 | 1009 | 0 | 0 | 0 | 0 | 0.2251 | 0.1889 | 1052 | 199 | 93 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
1 | 3005 | 0.72 | 228 | -1224 | -700 | 352 | 1009 | 0 | 0 | 0 | 0 | 0.2281 | 0.1915 | 1052 | 201 | 93.9 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3005 | 0.72 | 228 | -1224 | -700 | 353 | 1009 | 0 | 0 | 0 | 0 | 0.2281 | 0.1915 | 1053 | 202 | 94.4 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
2 | 3005 | 0.72 | 228 | -1234 | -700 | 353 | 1009 | 0 | 0 | 0 | 0 | 0.229 | 0.1922 | 1053 | 202 | 94.4 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3005 | 0.72 | 228 | -1234 | -699 | 351 | 1009 | 0 | 0 | 0 | 0 | 0.229 | 0.1922 | 1050 | 202 | 94.4 | 40 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
3 | 3005 | 0.72 | 228 | -1214 | -699 | 351 | 1009 | 0 | 0 | 0 | 0 | 0.2272 | 0.1907 | 1050 | 200 | 93.5 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3005 | 0.72 | 228 | -1214 | -705 | 353 | 1009 | 0 | 0 | 0 | 0 | 0.2272 | 0.1907 | 1058 | 202 | 94.4 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
4 | 3005 | 0.72 | 228 | -1214 | -705 | 353 | 1009 | 0 | 0 | 0 | 0 | 0.2272 | 0.1907 | 1058 | 202 | 94.4 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3005 | 0.72 | 228 | -1216 | -701 | 353 | 1009 | 0 | 0 | 0 | 0 | 0.2274 | 0.1909 | 1054 | 201 | 93.9 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
5 | 3005 | 0.72 | 228 | -1216 | -701 | 350 | 1009 | 0 | 0 | 0 | 0 | 0.2274 | 0.1909 | 1051 | 201 | 93.9 | 39 | Fan Tests | Backward Swept | 22.1 | 70 | 14 | 0.075 | 0.0044 | 0.96
Data Series 5
0 | 3005 | 0.69 | 219 | -944 | -574 | 483 | 1009 | 0 | 0 | 0 | 0 | 0.2003 | 0.1681 | 1057 | 178 | 86.8 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3005 | 0.69 | 219 | -992 | -574 | 483 | 1009 | 0 | 0 | 0 | 0 | 0.2054 | 0.1724 | 1057 | 182 | 88.8 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
1 | 3006 | 0.69 | 220 | -992 | -575 | 482 | 1009 | 0 | 0 | 0 | 0 | 0.2054 | 0.1724 | 1057 | 182 | 88.3 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3006 | 0.69 | 220 | -992 | -575 | 482 | 1009 | 0 | 0 | 0 | 0 | 0.2054 | 0.1724 | 1057 | 182 | 88.3 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
2 | 3006 | 0.69 | 220 | -992 | -575 | 479 | 1009 | 0 | 0 | 0 | 0 | 0.2054 | 0.1724 | 1054 | 182 | 88.3 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3006 | 0.69 | 220 | -1008 | -575 | 479 | 1009 | 0 | 0 | 0 | 0 | 0.207 | 0.1738 | 1054 | 183 | 88.8 | 38 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
3 | 3006 | 0.69 | 220 | -1008 | -575 | 479 | 1009 | 0 | 0 | 0 | 0 | 0.207 | 0.1738 | 1054 | 183 | 88.8 | 38 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3006 | 0.69 | 220 | -1008 | -575 | 478 | 1009 | 0 | 0 | 0 | 0 | 0.207 | 0.1738 | 1053 | 183 | 88.8 | 38 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
4 | 3006 | 0.69 | 220 | -934 | -575 | 478 | 1009 | 0 | 0 | 0 | 0 | 0.1993 | 0.1673 | 1053 | 176 | 85.4 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3006 | 0.69 | 220 | -934 | -575 | 483 | 1009 | 0 | 0 | 0 | 0 | 0.1993 | 0.1673 | 1058 | 177 | 85.9 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
5 | 3006 | 0.69 | 220 | -1008 | -579 | 483 | 1009 | 0 | 0 | 0 | 0 | 0.207 | 0.1738 | 1062 | 185 | 89.8 | 37 | Fan Tests | Backward Swept | 22.1 | 60 | 14 | 0.075 | 0.0044 | 0.96
Data Series 6
0 | 3006 | 0.64 | 202 | -724 | -428 | 634 | 1009 | 0 | 0 | 0 | 0 | 0.1754 | 0.1472 | 1062 | 156 | 83 | 34 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3006 | 0.64 | 202 | -714 | -419 | 634 | 1009 | 0 | 0 | 0 | 0 | 0.1742 | 0.1462 | 1053 | 154 | 81.9 | 34 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
1 | 3006 | 0.64 | 202 | -714 | -419 | 629 | 1009 | 0 | 0 | 0 | 0 | 0.1742 | 0.1462 | 1048 | 153 | 81.4 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3006 | 0.64 | 202 | -732 | -419 | 629 | 1009 | 0 | 0 | 0 | 0 | 0.1764 | 0.1481 | 1048 | 155 | 82.4 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
2 | 3006 | 0.64 | 202 | -732 | -427 | 626 | 1009 | 0 | 0 | 0 | 0 | 0.1764 | 0.1481 | 1053 | 156 | 83 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3006 | 0.64 | 202 | -732 | -427 | 626 | 1009 | 0 | 0 | 0 | 0 | 0.1764 | 0.1481 | 1053 | 156 | 83 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
3 | 3006 | 0.64 | 202 | -732 | -423 | 630 | 1009 | 0 | 0 | 0 | 0 | 0.1764 | 0.1481 | 1053 | 156 | 83 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3007 | 0.64 | 202 | -736 | -423 | 630 | 1009 | 0 | 0 | 0 | 0 | 0.1769 | 0.1485 | 1053 | 156 | 83 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
4 | 3007 | 0.64 | 202 | -736 | -418 | 630 | 1009 | 0 | 0 | 0 | 0 | 0.1769 | 0.1485 | 1048 | 156 | 83 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3007 | 0.64 | 202 | -736 | -418 | 629 | 1009 | 0 | 0 | 0 | 0 | 0.1769 | 0.1485 | 1047 | 155 | 82.4 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
5 | 3007 | 0.64 | 202 | -738 | -425 | 629 | 1009 | 0 | 0 | 0 | 0 | 0.1771 | 0.1487 | 1054 | 157 | 83.5 | 35 | Fan Tests | Backward Swept | 22.1 | 50 | 14 | 0.075 | 0.0044 | 0.96
Data Series 7
0 | 3008 | 0.57 | 182 | -478 | -279 | 754 | 1009 | 0 | 0 | 0 | 0 | 0.1426 | 0.1197 | 1033 | 124 | 73.8 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3008 | 0.57 | 182 | -476 | -279 | 754 | 1009 | 0 | 0 | 0 | 0 | 0.1423 | 0.1194 | 1033 | 123 | 73.2 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
1 | 3008 | 0.57 | 182 | -476 | -279 | 752 | 1009 | 0 | 0 | 0 | 0 | 0.1423 | 0.1194 | 1031 | 123 | 73.2 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3008 | 0.57 | 182 | -486 | -279 | 752 | 1009 | 0 | 0 | 0 | 0 | 0.1437 | 0.1206 | 1031 | 124 | 73.8 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
2 | 3008 | 0.57 | 182 | -486 | -284 | 752 | 1009 | 0 | 0 | 0 | 0 | 0.1437 | 0.1206 | 1036 | 125 | 74.4 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3008 | 0.57 | 182 | -484 | -284 | 752 | 1009 | 0 | 0 | 0 | 0 | 0.1434 | 0.1204 | 1036 | 125 | 74.4 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
3 | 3008 | 0.57 | 182 | -484 | -281 | 753 | 1009 | 0 | 0 | 0 | 0 | 0.1434 | 0.1204 | 1034 | 124 | 73.8 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3008 | 0.57 | 182 | -484 | -281 | 753 | 1009 | 0 | 0 | 0 | 0 | 0.1434 | 0.1204 | 1034 | 124 | 73.8 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
4 | 3008 | 0.57 | 182 | -484 | -278 | 753 | 1009 | 0 | 0 | 0 | 0 | 0.1434 | 0.1204 | 1031 | 124 | 73.8 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3008 | 0.57 | 182 | -484 | -278 | 751 | 1009 | 0 | 0 | 0 | 0 | 0.1434 | 0.1204 | 1029 | 124 | 73.8 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
5 | 3008 | 0.57 | 182 | -478 | -278 | 751 | 1009 | 0 | 0 | 0 | 0 | 0.1426 | 0.1197 | 1029 | 123 | 73.2 | 32 | Fan Tests | Backward Swept | 22.1 | 40 | 14 | 0.075 | 0.0044 | 0.96
Data Series 8
0 | 3009 | 0.51 | 162 | -270 | -167 | 837 | 1009 | 0 | 0 | 0 | 0 | 0.1071 | 0.0899 | 1004 | 90 | 60.8 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3009 | 0.5 | 159 | -270 | -167 | 836 | 1009 | 0 | 0 | 0 | 0 | 0.1071 | 0.0899 | 1003 | 90 | 62.1 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
1 | 3010 | 0.5 | 159 | -272 | -165 | 836 | 1009 | 0 | 0 | 0 | 0 | 0.1075 | 0.0902 | 1001 | 90 | 62.1 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3010 | 0.5 | 159 | -272 | -165 | 838 | 1009 | 0 | 0 | 0 | 0 | 0.1075 | 0.0902 | 1003 | 90 | 62.1 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
2 | 3010 | 0.5 | 159 | -276 | -165 | 838 | 1009 | 0 | 0 | 0 | 0 | 0.1083 | 0.0909 | 1003 | 91 | 62.8 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3010 | 0.5 | 159 | -276 | -168 | 839 | 1009 | 0 | 0 | 0 | 0 | 0.1083 | 0.0909 | 1007 | 92 | 63.4 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
3 | 3010 | 0.5 | 159 | -270 | -168 | 839 | 1009 | 0 | 0 | 0 | 0 | 0.1071 | 0.0899 | 1007 | 91 | 62.8 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3010 | 0.5 | 159 | -270 | -163 | 838 | 1009 | 0 | 0 | 0 | 0 | 0.1071 | 0.0899 | 1001 | 90 | 62.1 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
4 | 3010 | 0.5 | 159 | -270 | -163 | 838 | 1009 | 0 | 0 | 0 | 0 | 0.1071 | 0.0899 | 1001 | 90 | 62.1 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3010 | 0.5 | 159 | -270 | -167 | 838 | 1009 | 0 | 0 | 0 | 0 | 0.1071 | 0.0899 | 1005 | 90 | 62.1 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
5 | 3010 | 0.5 | 159 | -270 | -167 | 838 | 1009 | 0 | 0 | 0 | 0 | 0.1071 | 0.0899 | 1005 | 90 | 62.1 | 28 | Fan Tests | Backward Swept | 22.1 | 30 | 14 | 0.075 | 0.0044 | 0.96
Data Series 9
0 | 3012 | 0.43 | 136 | -130 | -85 | 868 | 1009 | 0 | 0 | 0 | 0 | 0.0743 | 0.0624 | 953 | 59 | 48.4 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3012 | 0.43 | 136 | -130 | -85 | 870 | 1009 | 0 | 0 | 0 | 0 | 0.0743 | 0.0624 | 955 | 60 | 49.2 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
1 | 3012 | 0.43 | 136 | -132 | -85 | 870 | 1009 | 0 | 0 | 0 | 0 | 0.0749 | 0.0629 | 955 | 60 | 49.2 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3012 | 0.43 | 136 | -132 | -86 | 871 | 1009 | 0 | 0 | 0 | 0 | 0.0749 | 0.0629 | 957 | 60 | 49.2 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
2 | 3012 | 0.43 | 136 | -132 | -86 | 871 | 1009 | 0 | 0 | 0 | 0 | 0.0749 | 0.0629 | 957 | 60 | 49.2 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3012 | 0.43 | 136 | -132 | -86 | 873 | 1009 | 0 | 0 | 0 | 0 | 0.0749 | 0.0629 | 959 | 60 | 49.2 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
3 | 3012 | 0.43 | 136 | -132 | -86 | 873 | 1009 | 0 | 0 | 0 | 0 | 0.0749 | 0.0629 | 959 | 60 | 49.2 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3012 | 0.43 | 136 | -132 | -86 | 873 | 1009 | 0 | 0 | 0 | 0 | 0.0749 | 0.0629 | 959 | 60 | 49.2 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
4 | 3012 | 0.43 | 136 | -132 | -86 | 870 | 1009 | 0 | 0 | 0 | 0 | 0.0749 | 0.0629 | 956 | 60 | 49.2 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3012 | 0.43 | 136 | -132 | -87 | 870 | 1009 | 0 | 0 | 0 | 0 | 0.0749 | 0.0629 | 957 | 60 | 49.2 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
5 | 3012 | 0.43 | 136 | -132 | -87 | 873 | 1009 | 0 | 0 | 0 | 0 | 0.0749 | 0.0629 | 960 | 60 | 49.2 | 24 | Fan Tests | Backward Swept | 22.1 | 20 | 14 | 0.075 | 0.0044 | 0.96
Data Series 10
0 | 3012 | 0.35 | 113 | -36 | -23 | 883 | 1009 | 0 | 0 | 0 | 0 | 0.0391 | 0.0328 | 906 | 30 | 30.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3013 | 0.35 | 113 | -36 | -24 | 883 | 1009 | 0 | 0 | 0 | 0 | 0.0391 | 0.0328 | 907 | 30 | 30.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
1 | 3013 | 0.35 | 113 | -36 | -24 | 883 | 1009 | 0 | 0 | 0 | 0 | 0.0391 | 0.0328 | 907 | 30 | 30.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3013 | 0.35 | 113 | -32 | -23 | 883 | 1009 | 0 | 0 | 0 | 0 | 0.0369 | 0.031 | 906 | 28 | 28.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
2 | 3013 | 0.35 | 113 | -32 | -23 | 885 | 1009 | 0 | 0 | 0 | 0 | 0.0369 | 0.031 | 908 | 28 | 28.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3013 | 0.35 | 113 | -34 | -23 | 885 | 1009 | 0 | 0 | 0 | 0 | 0.038 | 0.0319 | 908 | 29 | 29.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
3 | 3013 | 0.35 | 113 | -34 | -23 | 883 | 1009 | 0 | 0 | 0 | 0 | 0.038 | 0.0319 | 906 | 29 | 29.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3013 | 0.35 | 113 | -34 | -23 | 883 | 1009 | 0 | 0 | 0 | 0 | 0.038 | 0.0319 | 906 | 29 | 29.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
4 | 3013 | 0.35 | 113 | -34 | -23 | 883 | 1009 | 0 | 0 | 0 | 0 | 0.038 | 0.0319 | 906 | 29 | 29.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3013 | 0.35 | 113 | -34 | -23 | 883 | 1009 | 0 | 0 | 0 | 0 | 0.038 | 0.0319 | 906 | 29 | 29.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
5 | 3013 | 0.35 | 113 | -34 | -23 | 883 | 1009 | 0 | 0 | 0 | 0 | 0.038 | 0.0319 | 906 | 29 | 29.3 | 18 | Fan Tests | Backward Swept | 22.1 | 10 | 14 | 0.075 | 0.0044 | 0.96
Data Series 11
0 | 3013 | 0.3 | 95 | -2 | 42 | 929 | 1009 | 0 | 0 | 0 | 0 | 0.0092 | 0.0077 | 887 | 7 | 8.6 | 9 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96
0.5 | 3014 | 0.29 | 92 | -2 | 42 | 929 | 1009 | 0 | 0 | 0 | 0 | 0.0092 | 0.0077 | 887 | 7 | 9 | 9 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96
1 | 3014 | 0.29 | 92 | -2 | 42 | 924 | 1009 | 0 | 0 | 0 | 0 | 0.0092 | 0.0077 | 882 | 7 | 9 | 9 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96
1.5 | 3014 | 0.29 | 92 | -4 | 42 | 924 | 1009 | 0 | 0 | 0 | 0 | 0.013 | 0.0109 | 882 | 10 | 12.8 | 11 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96
2 | 3014 | 0.29 | 92 | -4 | 42 | 927 | 1009 | 0 | 0 | 0 | 0 | 0.013 | 0.0109 | 885 | 10 | 12.8 | 11 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96
2.5 | 3014 | 0.29 | 92 | -2 | 43 | 927 | 1009 | 0 | 0 | 0 | 0 | 0.0092 | 0.0077 | 884 | 7 | 9 | 9 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96
3 | 3014 | 0.29 | 92 | -2 | 43 | 929 | 1009 | 0 | 0 | 0 | 0 | 0.0092 | 0.0077 | 886 | 7 | 9 | 9 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96
3.5 | 3014 | 0.29 | 92 | 0 | 43 | 929 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 886 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96
4 | 3014 | 0.29 | 92 | 0 | 42 | 923 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 881 | 0 | 0 | 0 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96
4.5 | 3014 | 0.29 | 92 | -2 | 42 | 923 | 1009 | 0 | 0 | 0 | 0 | 0.0092 | 0.0077 | 881 | 7 | 9 | 9 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96
5 | 3014 | 0.29 | 92 | -2 | 41 | 926 | 1009 | 0 | 0 | 0 | 0 | 0.0092 | 0.0077 | 885 | 7 | 9 | 9 | Fan Tests | Backward Swept | 22.1 | 0 | 14 | 0.075 | 0.0044 | 0.96