## VDAS Data
Time | MFP100 1.5kW Motor Drive |  |  | DP3 Digital Pressure Display |  |  |  | Analogue Input Board |  |  |  | Calculated Parameters | [5 empty] | Test Conditions |  |  |  |  | Nozzle Parameters
Time | Speed | Torque | Power | D P1 | P2 | P3 | P4 [Absolute] | Voltage 1 | Current 1 | Voltage 2 | Current 2 | Mass Flow Rate | Volumetric Flow Rate | Fan Total Pressure | Air Power | Fan Efficiency | Specific Speed | Configuration | Impeller | Ambient Temperature | Slide Valve Position | Mechanical Power Loss | Nozzle Diameter | Nozzle Area | Nozzle Discharge Coefficient
(s) | (rev.min-1) | (Nm) | (W) | (Pa) | (Pa) | (Pa) | (mbar) | (V) | (mA) | (V) | (mA) | (kg.s-1) | (m3.s-1) | (Pa) | (W) | (%) | (rev.min-1) |  |  | (°C) | (%) | (W) | (m) | (m2)
Data Series 1
0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1499 | 0.4 | 63 | -492 | -258 | 33 | 1021 | 0 | 0 | 0 | 0 | 0.1455 | 0.1207 | 291 | 35 | 60.3 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
1 | 1499 | 0.4 | 63 | -492 | -258 | 33 | 1022 | 0 | 0 | 0 | 0 | 0.1456 | 0.1207 | 291 | 35 | 60.3 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1499 | 0.4 | 63 | -492 | -257 | 34 | 1022 | 0 | 0 | 0 | 0 | 0.1456 | 0.1207 | 291 | 35 | 60.3 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
2 | 1499 | 0.4 | 63 | -492 | -257 | 34 | 1021 | 0 | 0 | 0 | 0 | 0.1455 | 0.1207 | 291 | 35 | 60.3 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1499 | 0.4 | 63 | -486 | -258 | 34 | 1021 | 0 | 0 | 0 | 0 | 0.1446 | 0.1199 | 292 | 35 | 60.3 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
3 | 1499 | 0.4 | 63 | -486 | -258 | 34 | 1021 | 0 | 0 | 0 | 0 | 0.1446 | 0.1199 | 292 | 35 | 60.3 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1499 | 0.4 | 63 | -490 | -258 | 34 | 1021 | 0 | 0 | 0 | 0 | 0.1452 | 0.1204 | 292 | 35 | 60.3 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
4 | 1499 | 0.39 | 62 | -490 | -258 | 33 | 1021 | 0 | 0 | 0 | 0 | 0.1452 | 0.1204 | 291 | 35 | 61.4 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1499 | 0.39 | 62 | -478 | -258 | 33 | 1021 | 0 | 0 | 0 | 0 | 0.1434 | 0.119 | 291 | 35 | 61.4 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
5 | 1499 | 0.39 | 62 | -478 | -257 | 33 | 1021 | 0 | 0 | 0 | 0 | 0.1434 | 0.119 | 290 | 35 | 61.4 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 5 | 0.075 | 0.0044 | 0.96
Data Series 2
0 | 1499 | 0.4 | 63 | -474 | -250 | 43 | 1022 | 0 | 0 | 0 | 0 | 0.1429 | 0.1184 | 293 | 35 | 60.3 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1499 | 0.4 | 63 | -474 | -250 | 43 | 1022 | 0 | 0 | 0 | 0 | 0.1429 | 0.1184 | 293 | 35 | 60.3 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
1 | 1499 | 0.4 | 63 | -468 | -249 | 43 | 1022 | 0 | 0 | 0 | 0 | 0.142 | 0.1177 | 292 | 34 | 58.6 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1499 | 0.4 | 63 | -468 | -249 | 43 | 1021 | 0 | 0 | 0 | 0 | 0.1419 | 0.1177 | 292 | 34 | 58.6 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
2 | 1499 | 0.39 | 62 | -464 | -249 | 43 | 1021 | 0 | 0 | 0 | 0 | 0.1413 | 0.1172 | 292 | 34 | 59.6 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1499 | 0.39 | 62 | -464 | -249 | 42 | 1021 | 0 | 0 | 0 | 0 | 0.1413 | 0.1172 | 291 | 34 | 59.6 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
3 | 1499 | 0.39 | 62 | -462 | -249 | 42 | 1021 | 0 | 0 | 0 | 0 | 0.141 | 0.117 | 291 | 34 | 59.6 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1499 | 0.38 | 60 | -462 | -249 | 43 | 1021 | 0 | 0 | 0 | 0 | 0.141 | 0.117 | 292 | 34 | 61.8 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
4 | 1499 | 0.39 | 62 | -476 | -249 | 43 | 1021 | 0 | 0 | 0 | 0 | 0.1431 | 0.1187 | 292 | 35 | 61.4 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1499 | 0.39 | 62 | -476 | -250 | 42 | 1021 | 0 | 0 | 0 | 0 | 0.1431 | 0.1187 | 292 | 35 | 61.4 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
5 | 1499 | 0.39 | 62 | -476 | -250 | 42 | 1022 | 0 | 0 | 0 | 0 | 0.1432 | 0.1187 | 292 | 35 | 61.4 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 5 | 0.075 | 0.0044 | 0.96
Data Series 3
0 | 1499 | 0.39 | 62 | -430 | -230 | 69 | 1021 | 0 | 0 | 0 | 0 | 0.136 | 0.1128 | 299 | 34 | 59.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1499 | 0.39 | 62 | -430 | -230 | 69 | 1021 | 0 | 0 | 0 | 0 | 0.136 | 0.1128 | 299 | 34 | 59.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
1 | 1499 | 0.39 | 62 | -432 | -231 | 69 | 1021 | 0 | 0 | 0 | 0 | 0.1363 | 0.1131 | 300 | 34 | 59.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1499 | 0.39 | 62 | -432 | -231 | 69 | 1021 | 0 | 0 | 0 | 0 | 0.1363 | 0.1131 | 300 | 34 | 59.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
2 | 1499 | 0.39 | 62 | -432 | -230 | 69 | 1021 | 0 | 0 | 0 | 0 | 0.1363 | 0.1131 | 299 | 34 | 59.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1499 | 0.39 | 62 | -432 | -230 | 68 | 1021 | 0 | 0 | 0 | 0 | 0.1363 | 0.1131 | 298 | 34 | 59.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
3 | 1499 | 0.39 | 62 | -430 | -230 | 68 | 1021 | 0 | 0 | 0 | 0 | 0.136 | 0.1128 | 298 | 34 | 59.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1499 | 0.39 | 62 | -430 | -229 | 68 | 1021 | 0 | 0 | 0 | 0 | 0.136 | 0.1128 | 297 | 34 | 59.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
4 | 1499 | 0.39 | 62 | -428 | -229 | 68 | 1021 | 0 | 0 | 0 | 0 | 0.1357 | 0.1126 | 297 | 33 | 57.9 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1499 | 0.39 | 62 | -428 | -231 | 67 | 1021 | 0 | 0 | 0 | 0 | 0.1357 | 0.1126 | 298 | 34 | 59.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
5 | 1499 | 0.39 | 62 | -432 | -231 | 67 | 1021 | 0 | 0 | 0 | 0 | 0.1363 | 0.1131 | 298 | 34 | 59.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 5 | 0.075 | 0.0044 | 0.96
Data Series 4
0 | 1499 | 0.38 | 60 | -366 | -198 | 105 | 1021 | 0 | 0 | 0 | 0 | 0.1255 | 0.1041 | 303 | 32 | 58.2 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1499 | 0.38 | 60 | -368 | -200 | 105 | 1021 | 0 | 0 | 0 | 0 | 0.1258 | 0.1044 | 305 | 32 | 58.2 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
1 | 1499 | 0.38 | 60 | -368 | -200 | 104 | 1022 | 0 | 0 | 0 | 0 | 0.1259 | 0.1043 | 304 | 32 | 58.2 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1499 | 0.37 | 59 | -368 | -200 | 104 | 1022 | 0 | 0 | 0 | 0 | 0.1259 | 0.1043 | 304 | 32 | 59.3 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
2 | 1499 | 0.37 | 59 | -368 | -198 | 105 | 1022 | 0 | 0 | 0 | 0 | 0.1259 | 0.1043 | 303 | 32 | 59.3 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1499 | 0.37 | 59 | -364 | -198 | 105 | 1021 | 0 | 0 | 0 | 0 | 0.1251 | 0.1038 | 303 | 31 | 57.4 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
3 | 1499 | 0.37 | 59 | -364 | -198 | 104 | 1021 | 0 | 0 | 0 | 0 | 0.1251 | 0.1038 | 302 | 31 | 57.4 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1499 | 0.37 | 59 | -366 | -198 | 104 | 1022 | 0 | 0 | 0 | 0 | 0.1255 | 0.104 | 302 | 31 | 57.4 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
4 | 1499 | 0.37 | 59 | -366 | -197 | 104 | 1022 | 0 | 0 | 0 | 0 | 0.1255 | 0.104 | 301 | 31 | 57.4 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1499 | 0.37 | 59 | -366 | -197 | 104 | 1022 | 0 | 0 | 0 | 0 | 0.1255 | 0.104 | 301 | 31 | 57.4 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
5 | 1499 | 0.37 | 59 | -360 | -200 | 104 | 1022 | 0 | 0 | 0 | 0 | 0.1245 | 0.1032 | 304 | 31 | 57.4 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 5 | 0.075 | 0.0044 | 0.96
Data Series 5
0 | 1499 | 0.36 | 57 | -286 | -161 | 145 | 1021 | 0 | 0 | 0 | 0 | 0.1109 | 0.092 | 306 | 28 | 53.8 | 34 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1499 | 0.36 | 57 | -286 | -161 | 145 | 1021 | 0 | 0 | 0 | 0 | 0.1109 | 0.092 | 306 | 28 | 53.8 | 34 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
1 | 1499 | 0.36 | 57 | -286 | -161 | 143 | 1021 | 0 | 0 | 0 | 0 | 0.1109 | 0.092 | 304 | 28 | 53.8 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1499 | 0.36 | 57 | -286 | -160 | 143 | 1021 | 0 | 0 | 0 | 0 | 0.1109 | 0.092 | 303 | 28 | 53.8 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
2 | 1499 | 0.36 | 57 | -286 | -160 | 144 | 1021 | 0 | 0 | 0 | 0 | 0.1109 | 0.092 | 304 | 28 | 53.8 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1499 | 0.37 | 59 | -290 | -161 | 144 | 1021 | 0 | 0 | 0 | 0 | 0.1117 | 0.0927 | 305 | 28 | 51.9 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
3 | 1499 | 0.35 | 56 | -290 | -161 | 144 | 1021 | 0 | 0 | 0 | 0 | 0.1117 | 0.0927 | 305 | 28 | 54.9 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1499 | 0.36 | 57 | -298 | -161 | 144 | 1021 | 0 | 0 | 0 | 0 | 0.1132 | 0.0939 | 305 | 29 | 55.8 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
4 | 1499 | 0.35 | 56 | -298 | -162 | 143 | 1021 | 0 | 0 | 0 | 0 | 0.1132 | 0.0939 | 305 | 29 | 56.9 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1499 | 0.35 | 56 | -284 | -162 | 143 | 1022 | 0 | 0 | 0 | 0 | 0.1106 | 0.0917 | 305 | 28 | 54.9 | 34 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
5 | 1499 | 0.35 | 56 | -284 | -162 | 143 | 1022 | 0 | 0 | 0 | 0 | 0.1106 | 0.0917 | 305 | 28 | 54.9 | 34 | Fan Tests | Radial Swept | 22.1 | 60 | 5 | 0.075 | 0.0044 | 0.96
Data Series 6
0 | 1499 | 0.34 | 53 | -200 | -115 | 183 | 1021 | 0 | 0 | 0 | 0 | 0.0928 | 0.077 | 298 | 23 | 47.9 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1499 | 0.34 | 53 | -200 | -115 | 183 | 1021 | 0 | 0 | 0 | 0 | 0.0928 | 0.077 | 298 | 23 | 47.9 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
1 | 1499 | 0.33 | 51 | -200 | -115 | 184 | 1021 | 0 | 0 | 0 | 0 | 0.0928 | 0.077 | 299 | 23 | 50 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1499 | 0.33 | 51 | -200 | -115 | 184 | 1021 | 0 | 0 | 0 | 0 | 0.0928 | 0.077 | 299 | 23 | 50 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
2 | 1499 | 0.33 | 51 | -200 | -113 | 183 | 1021 | 0 | 0 | 0 | 0 | 0.0928 | 0.077 | 296 | 23 | 50 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1499 | 0.33 | 51 | -200 | -113 | 183 | 1021 | 0 | 0 | 0 | 0 | 0.0928 | 0.077 | 296 | 23 | 50 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
3 | 1499 | 0.33 | 51 | -200 | -115 | 183 | 1021 | 0 | 0 | 0 | 0 | 0.0928 | 0.077 | 298 | 23 | 50 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1499 | 0.34 | 53 | -202 | -115 | 183 | 1021 | 0 | 0 | 0 | 0 | 0.0932 | 0.0773 | 298 | 23 | 47.9 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
4 | 1499 | 0.33 | 51 | -202 | -116 | 183 | 1021 | 0 | 0 | 0 | 0 | 0.0932 | 0.0773 | 299 | 23 | 50 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1499 | 0.34 | 53 | -202 | -116 | 183 | 1022 | 0 | 0 | 0 | 0 | 0.0933 | 0.0773 | 299 | 23 | 47.9 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
5 | 1499 | 0.34 | 53 | -198 | -116 | 183 | 1022 | 0 | 0 | 0 | 0 | 0.0923 | 0.0765 | 299 | 23 | 47.9 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 5 | 0.075 | 0.0044 | 0.96
Data Series 7
0 | 1500 | 0.3 | 47 | -126 | -74 | 211 | 1021 | 0 | 0 | 0 | 0 | 0.0736 | 0.0611 | 285 | 17 | 40.5 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1500 | 0.3 | 47 | -128 | -74 | 211 | 1021 | 0 | 0 | 0 | 0 | 0.0742 | 0.0616 | 285 | 18 | 42.9 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
1 | 1500 | 0.3 | 47 | -128 | -75 | 209 | 1021 | 0 | 0 | 0 | 0 | 0.0742 | 0.0616 | 284 | 17 | 40.5 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1500 | 0.3 | 47 | -132 | -75 | 209 | 1022 | 0 | 0 | 0 | 0 | 0.0754 | 0.0625 | 284 | 18 | 42.9 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
2 | 1500 | 0.3 | 47 | -132 | -75 | 210 | 1022 | 0 | 0 | 0 | 0 | 0.0754 | 0.0625 | 285 | 18 | 42.9 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1500 | 0.3 | 47 | -132 | -75 | 210 | 1021 | 0 | 0 | 0 | 0 | 0.0754 | 0.0625 | 285 | 18 | 42.9 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
3 | 1500 | 0.3 | 47 | -130 | -75 | 210 | 1021 | 0 | 0 | 0 | 0 | 0.0748 | 0.062 | 285 | 18 | 42.9 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1500 | 0.3 | 47 | -130 | -75 | 211 | 1022 | 0 | 0 | 0 | 0 | 0.0748 | 0.062 | 286 | 18 | 42.9 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
4 | 1500 | 0.3 | 47 | -132 | -75 | 211 | 1022 | 0 | 0 | 0 | 0 | 0.0754 | 0.0625 | 286 | 18 | 42.9 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1500 | 0.3 | 47 | -132 | -75 | 212 | 1021 | 0 | 0 | 0 | 0 | 0.0754 | 0.0625 | 287 | 18 | 42.9 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
5 | 1500 | 0.3 | 47 | -126 | -75 | 212 | 1021 | 0 | 0 | 0 | 0 | 0.0736 | 0.0611 | 287 | 18 | 42.9 | 29 | Fan Tests | Radial Swept | 22.1 | 40 | 5 | 0.075 | 0.0044 | 0.96
Data Series 8
0 | 1500 | 0.27 | 43 | -72 | -44 | 224 | 1021 | 0 | 0 | 0 | 0 | 0.0557 | 0.0462 | 268 | 12 | 31.6 | 27 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1500 | 0.27 | 43 | -74 | -44 | 224 | 1021 | 0 | 0 | 0 | 0 | 0.0564 | 0.0468 | 268 | 13 | 34.2 | 27 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
1 | 1500 | 0.27 | 43 | -74 | -46 | 226 | 1021 | 0 | 0 | 0 | 0 | 0.0564 | 0.0468 | 272 | 13 | 34.2 | 27 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1500 | 0.27 | 43 | -68 | -46 | 226 | 1021 | 0 | 0 | 0 | 0 | 0.0541 | 0.0449 | 272 | 12 | 31.6 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
2 | 1500 | 0.27 | 43 | -68 | -45 | 226 | 1021 | 0 | 0 | 0 | 0 | 0.0541 | 0.0449 | 271 | 12 | 31.6 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1500 | 0.26 | 41 | -68 | -45 | 227 | 1022 | 0 | 0 | 0 | 0 | 0.0541 | 0.0448 | 272 | 12 | 33.3 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
3 | 1500 | 0.27 | 43 | -68 | -46 | 227 | 1022 | 0 | 0 | 0 | 0 | 0.0541 | 0.0448 | 273 | 12 | 31.6 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1500 | 0.26 | 41 | -68 | -46 | 226 | 1021 | 0 | 0 | 0 | 0 | 0.0541 | 0.0449 | 272 | 12 | 33.3 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
4 | 1500 | 0.26 | 41 | -68 | -45 | 226 | 1021 | 0 | 0 | 0 | 0 | 0.0541 | 0.0449 | 271 | 12 | 33.3 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1500 | 0.26 | 41 | -68 | -45 | 226 | 1021 | 0 | 0 | 0 | 0 | 0.0541 | 0.0449 | 271 | 12 | 33.3 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
5 | 1500 | 0.26 | 41 | -70 | -45 | 226 | 1021 | 0 | 0 | 0 | 0 | 0.0549 | 0.0455 | 271 | 12 | 33.3 | 27 | Fan Tests | Radial Swept | 22.1 | 30 | 5 | 0.075 | 0.0044 | 0.96
Data Series 9
0 | 1500 | 0.24 | 39 | -32 | -23 | 235 | 1022 | 0 | 0 | 0 | 0 | 0.0371 | 0.0307 | 258 | 8 | 23.5 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1500 | 0.24 | 39 | -34 | -23 | 235 | 1022 | 0 | 0 | 0 | 0 | 0.0383 | 0.0317 | 258 | 8 | 23.5 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
1 | 1500 | 0.24 | 39 | -34 | -23 | 234 | 1022 | 0 | 0 | 0 | 0 | 0.0383 | 0.0317 | 257 | 8 | 23.5 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1500 | 0.24 | 39 | -36 | -23 | 234 | 1021 | 0 | 0 | 0 | 0 | 0.0394 | 0.0327 | 257 | 8 | 23.5 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
2 | 1500 | 0.25 | 40 | -36 | -23 | 236 | 1021 | 0 | 0 | 0 | 0 | 0.0394 | 0.0327 | 259 | 8 | 22.9 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1500 | 0.24 | 39 | -36 | -23 | 236 | 1021 | 0 | 0 | 0 | 0 | 0.0394 | 0.0327 | 259 | 8 | 23.5 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
3 | 1500 | 0.25 | 40 | -36 | -24 | 236 | 1021 | 0 | 0 | 0 | 0 | 0.0394 | 0.0327 | 260 | 9 | 25.7 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1500 | 0.24 | 39 | -36 | -24 | 235 | 1021 | 0 | 0 | 0 | 0 | 0.0394 | 0.0327 | 259 | 8 | 23.5 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
4 | 1500 | 0.24 | 39 | -36 | -23 | 235 | 1021 | 0 | 0 | 0 | 0 | 0.0394 | 0.0327 | 258 | 8 | 23.5 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.24 | 39 | -36 | -23 | 235 | 1021 | 0 | 0 | 0 | 0 | 0.0394 | 0.0327 | 258 | 8 | 23.5 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.24 | 39 | -34 | -23 | 235 | 1021 | 0 | 0 | 0 | 0 | 0.0382 | 0.0317 | 258 | 8 | 23.5 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 5 | 0.075 | 0.0044 | 0.96
Data Series 10
0 | 1501 | 0.22 | 36 | -8 | -2 | 242 | 1021 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 244 | 4 | 12.9 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1501 | 0.22 | 34 | -8 | -3 | 242 | 1021 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 245 | 4 | 13.8 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
1 | 1501 | 0.22 | 34 | -8 | -3 | 242 | 1021 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 245 | 4 | 13.8 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.22 | 34 | -8 | -3 | 242 | 1021 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 245 | 4 | 13.8 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.22 | 34 | -8 | -3 | 244 | 1022 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 247 | 4 | 13.8 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.22 | 34 | -8 | -3 | 244 | 1022 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 247 | 4 | 13.8 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.22 | 34 | -8 | -3 | 242 | 1021 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 245 | 4 | 13.8 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.22 | 34 | -8 | -3 | 242 | 1021 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 245 | 4 | 13.8 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.22 | 34 | -8 | -3 | 241 | 1021 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 244 | 4 | 13.8 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.22 | 34 | -8 | -3 | 241 | 1022 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 244 | 4 | 13.8 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.22 | 34 | -8 | -1 | 241 | 1022 | 0 | 0 | 0 | 0 | 0.0186 | 0.0154 | 242 | 4 | 13.8 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 5 | 0.075 | 0.0044 | 0.96
Data Series 11
0 | 1501 | 0.21 | 33 | 0 | 11 | 253 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
0.5 | 1501 | 0.21 | 33 | 0 | 12 | 253 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
1 | 1501 | 0.21 | 33 | 0 | 12 | 253 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
1.5 | 1501 | 0.21 | 33 | 0 | 11 | 253 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
2 | 1501 | 0.21 | 33 | 0 | 11 | 253 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
2.5 | 1501 | 0.21 | 33 | 0 | 11 | 253 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
3 | 1501 | 0.21 | 33 | 0 | 11 | 251 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
3.5 | 1501 | 0.21 | 33 | 0 | 11 | 251 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
4 | 1501 | 0.21 | 33 | 0 | 11 | 254 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
4.5 | 1501 | 0.21 | 33 | 0 | 12 | 254 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96
5 | 1501 | 0.21 | 33 | 0 | 12 | 253 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 5 | 0.075 | 0.0044 | 0.96