## VDAS Data
Time | MFP100 1.5kW Motor Drive |  |  | DP3 Digital Pressure Display |  |  |  | Analogue Input Board |  |  |  | Calculated Parameters | [5 empty] | Test Conditions |  |  |  |  | Nozzle Parameters
Time | Speed | Torque | Power | D P1 | P2 | P3 | P4 [Absolute] | Voltage 1 | Current 1 | Voltage 2 | Current 2 | Mass Flow Rate | Volumetric Flow Rate | Fan Total Pressure | Air Power | Fan Efficiency | Specific Speed | Configuration | Impeller | Ambient Temperature | Slide Valve Position | Mechanical Power Loss | Nozzle Diameter | Nozzle Area | Nozzle Discharge Coefficient
(s) | (rev.min-1) | (Nm) | (W) | (Pa) | (Pa) | (Pa) | (mbar) | (V) | (mA) | (V) | (mA) | (kg.s-1) | (m3.s-1) | (Pa) | (W) | (%) | (rev.min-1) |  |  | (°C) | (%) | (W) | (m) | (m2)
Data Series 1
0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2505 | 0.9 | 236 | -1316 | -697 | 111 | 1021 | 0 | 0 | 0 | 0 | 0.2379 | 0.1973 | 808 | 159 | 71 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
1 | 2505 | 0.9 | 236 | -1316 | -697 | 111 | 1021 | 0 | 0 | 0 | 0 | 0.2379 | 0.1973 | 808 | 159 | 71 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2506 | 0.9 | 236 | -1362 | -700 | 111 | 1021 | 0 | 0 | 0 | 0 | 0.2421 | 0.2008 | 811 | 163 | 72.8 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
2 | 2505 | 0.9 | 236 | -1362 | -700 | 112 | 1021 | 0 | 0 | 0 | 0 | 0.2421 | 0.2008 | 812 | 163 | 72.8 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2505 | 0.9 | 236 | -1270 | -697 | 112 | 1021 | 0 | 0 | 0 | 0 | 0.2337 | 0.1939 | 809 | 157 | 70.1 | 40 | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
3 | 2504 | 0.9 | 236 | -1270 | -697 | 110 | 1021 | 0 | 0 | 0 | 0 | 0.2337 | 0.1939 | 807 | 156 | 69.6 | 40 | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2504 | 0.9 | 236 | -1306 | -697 | 110 | 1021 | 0 | 0 | 0 | 0 | 0.237 | 0.1966 | 807 | 159 | 71 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
4 | 2505 | 0.9 | 236 | -1306 | -705 | 111 | 1021 | 0 | 0 | 0 | 0 | 0.237 | 0.1966 | 816 | 160 | 71.4 | 40 | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2505 | 0.9 | 236 | -1338 | -705 | 111 | 1021 | 0 | 0 | 0 | 0 | 0.2399 | 0.199 | 816 | 162 | 72.3 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
5 | 2506 | 0.9 | 236 | -1338 | -700 | 116 | 1021 | 0 | 0 | 0 | 0 | 0.2399 | 0.199 | 816 | 162 | 72.3 | 41 | Fan Tests | Radial Swept | 22.1 | 100 | 12 | 0.075 | 0.0044 | 0.96
Data Series 2
0 | 2505 | 0.9 | 236 | -1350 | -684 | 133 | 1021 | 0 | 0 | 0 | 0 | 0.241 | 0.1999 | 817 | 163 | 72.8 | 41 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2505 | 0.9 | 236 | -1294 | -687 | 133 | 1021 | 0 | 0 | 0 | 0 | 0.2359 | 0.1957 | 820 | 160 | 71.4 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
1 | 2504 | 0.9 | 236 | -1294 | -687 | 132 | 1021 | 0 | 0 | 0 | 0 | 0.2359 | 0.1957 | 819 | 160 | 71.4 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2504 | 0.9 | 236 | -1340 | -684 | 132 | 1021 | 0 | 0 | 0 | 0 | 0.2401 | 0.1992 | 816 | 163 | 72.8 | 41 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
2 | 2505 | 0.9 | 236 | -1340 | -684 | 133 | 1021 | 0 | 0 | 0 | 0 | 0.2401 | 0.1992 | 817 | 163 | 72.8 | 41 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2505 | 0.9 | 236 | -1314 | -684 | 133 | 1021 | 0 | 0 | 0 | 0 | 0.2378 | 0.1973 | 817 | 161 | 71.9 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
3 | 2505 | 0.89 | 234 | -1314 | -685 | 133 | 1021 | 0 | 0 | 0 | 0 | 0.2378 | 0.1973 | 818 | 161 | 72.5 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2505 | 0.9 | 236 | -1288 | -685 | 133 | 1021 | 0 | 0 | 0 | 0 | 0.2354 | 0.1953 | 818 | 160 | 71.4 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
4 | 2506 | 0.9 | 236 | -1288 | -686 | 132 | 1021 | 0 | 0 | 0 | 0 | 0.2354 | 0.1953 | 818 | 160 | 71.4 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2505 | 0.9 | 236 | -1314 | -686 | 132 | 1022 | 0 | 0 | 0 | 0 | 0.2379 | 0.1971 | 818 | 161 | 71.9 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
5 | 2505 | 0.9 | 236 | -1314 | -686 | 132 | 1022 | 0 | 0 | 0 | 0 | 0.2379 | 0.1971 | 818 | 161 | 71.9 | 40 | Fan Tests | Radial Swept | 22.1 | 90 | 12 | 0.075 | 0.0044 | 0.96
Data Series 3
0 | 2506 | 0.88 | 231 | -1184 | -629 | 206 | 1022 | 0 | 0 | 0 | 0 | 0.2258 | 0.1871 | 835 | 156 | 71.2 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2505 | 0.88 | 231 | -1188 | -629 | 206 | 1021 | 0 | 0 | 0 | 0 | 0.2261 | 0.1876 | 835 | 157 | 71.7 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
1 | 2505 | 0.88 | 231 | -1188 | -627 | 203 | 1021 | 0 | 0 | 0 | 0 | 0.2261 | 0.1876 | 830 | 156 | 71.2 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2505 | 0.88 | 231 | -1194 | -627 | 203 | 1021 | 0 | 0 | 0 | 0 | 0.2266 | 0.188 | 830 | 156 | 71.2 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
2 | 2505 | 0.88 | 231 | -1194 | -629 | 203 | 1021 | 0 | 0 | 0 | 0 | 0.2266 | 0.188 | 832 | 156 | 71.2 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2506 | 0.88 | 231 | -1194 | -629 | 202 | 1021 | 0 | 0 | 0 | 0 | 0.2266 | 0.188 | 831 | 156 | 71.2 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
3 | 2506 | 0.88 | 231 | -1164 | -628 | 202 | 1021 | 0 | 0 | 0 | 0 | 0.2238 | 0.1856 | 830 | 154 | 70.3 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2506 | 0.88 | 231 | -1164 | -628 | 204 | 1021 | 0 | 0 | 0 | 0 | 0.2238 | 0.1856 | 832 | 154 | 70.3 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
4 | 2505 | 0.88 | 231 | -1242 | -631 | 204 | 1021 | 0 | 0 | 0 | 0 | 0.2311 | 0.1917 | 835 | 160 | 73.1 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2506 | 0.88 | 231 | -1242 | -631 | 202 | 1021 | 0 | 0 | 0 | 0 | 0.2311 | 0.1917 | 833 | 160 | 73.1 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
5 | 2505 | 0.88 | 231 | -1230 | -631 | 202 | 1021 | 0 | 0 | 0 | 0 | 0.23 | 0.1908 | 833 | 159 | 72.6 | 39 | Fan Tests | Radial Swept | 22.1 | 80 | 12 | 0.075 | 0.0044 | 0.96
Data Series 4
0 | 2506 | 0.85 | 224 | -1056 | -544 | 302 | 1022 | 0 | 0 | 0 | 0 | 0.2132 | 0.1767 | 846 | 149 | 70.3 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2506 | 0.85 | 224 | -1056 | -544 | 299 | 1021 | 0 | 0 | 0 | 0 | 0.2131 | 0.1768 | 843 | 149 | 70.3 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
1 | 2506 | 0.85 | 224 | -1056 | -547 | 299 | 1021 | 0 | 0 | 0 | 0 | 0.2131 | 0.1768 | 846 | 150 | 70.8 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2506 | 0.85 | 224 | -1056 | -547 | 300 | 1022 | 0 | 0 | 0 | 0 | 0.2132 | 0.1767 | 847 | 150 | 70.8 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
2 | 2505 | 0.85 | 224 | -1048 | -547 | 300 | 1022 | 0 | 0 | 0 | 0 | 0.2124 | 0.176 | 847 | 149 | 70.3 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2506 | 0.85 | 224 | -1048 | -542 | 300 | 1022 | 0 | 0 | 0 | 0 | 0.2124 | 0.176 | 842 | 148 | 69.8 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
3 | 2506 | 0.85 | 224 | -1056 | -542 | 300 | 1022 | 0 | 0 | 0 | 0 | 0.2132 | 0.1767 | 842 | 149 | 70.3 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2506 | 0.85 | 224 | -1056 | -546 | 299 | 1022 | 0 | 0 | 0 | 0 | 0.2132 | 0.1767 | 845 | 149 | 70.3 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
4 | 2506 | 0.85 | 224 | -1032 | -546 | 299 | 1022 | 0 | 0 | 0 | 0 | 0.2108 | 0.1747 | 845 | 148 | 69.8 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2506 | 0.84 | 222 | -1032 | -545 | 299 | 1022 | 0 | 0 | 0 | 0 | 0.2108 | 0.1747 | 844 | 147 | 70 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
5 | 2506 | 0.84 | 222 | -1032 | -545 | 301 | 1021 | 0 | 0 | 0 | 0 | 0.2107 | 0.1748 | 846 | 148 | 70.5 | 37 | Fan Tests | Radial Swept | 22.1 | 70 | 12 | 0.075 | 0.0044 | 0.96
Data Series 5
0 | 2507 | 0.8 | 210 | -838 | -436 | 410 | 1021 | 0 | 0 | 0 | 0 | 0.1899 | 0.1575 | 846 | 133 | 67.2 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2507 | 0.8 | 210 | -838 | -438 | 410 | 1021 | 0 | 0 | 0 | 0 | 0.1899 | 0.1575 | 848 | 134 | 67.7 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
1 | 2507 | 0.79 | 207 | -838 | -438 | 410 | 1022 | 0 | 0 | 0 | 0 | 0.19 | 0.1575 | 848 | 134 | 68.7 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2506 | 0.8 | 210 | -850 | -437 | 410 | 1022 | 0 | 0 | 0 | 0 | 0.1913 | 0.1585 | 847 | 134 | 67.7 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
2 | 2507 | 0.8 | 210 | -850 | -437 | 411 | 1021 | 0 | 0 | 0 | 0 | 0.1912 | 0.1586 | 848 | 134 | 67.7 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2506 | 0.8 | 210 | -852 | -437 | 411 | 1021 | 0 | 0 | 0 | 0 | 0.1914 | 0.1588 | 848 | 135 | 68.2 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
3 | 2506 | 0.8 | 210 | -852 | -437 | 414 | 1021 | 0 | 0 | 0 | 0 | 0.1914 | 0.1588 | 851 | 135 | 68.2 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2506 | 0.8 | 210 | -848 | -437 | 414 | 1021 | 0 | 0 | 0 | 0 | 0.191 | 0.1584 | 851 | 135 | 68.2 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
4 | 2506 | 0.8 | 210 | -848 | -438 | 410 | 1021 | 0 | 0 | 0 | 0 | 0.191 | 0.1584 | 848 | 134 | 67.7 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2506 | 0.8 | 210 | -846 | -438 | 410 | 1022 | 0 | 0 | 0 | 0 | 0.1909 | 0.1582 | 848 | 134 | 67.7 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
5 | 2506 | 0.8 | 210 | -846 | -437 | 413 | 1022 | 0 | 0 | 0 | 0 | 0.1909 | 0.1582 | 850 | 134 | 67.7 | 35 | Fan Tests | Radial Swept | 22.1 | 60 | 12 | 0.075 | 0.0044 | 0.96
Data Series 6
0 | 2508 | 0.72 | 190 | -584 | -306 | 527 | 1021 | 0 | 0 | 0 | 0 | 0.1585 | 0.1315 | 833 | 110 | 61.8 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2508 | 0.71 | 188 | -584 | -306 | 528 | 1022 | 0 | 0 | 0 | 0 | 0.1586 | 0.1314 | 834 | 110 | 62.5 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
1 | 2508 | 0.71 | 188 | -586 | -302 | 528 | 1022 | 0 | 0 | 0 | 0 | 0.1589 | 0.1317 | 830 | 109 | 61.9 | 33 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2508 | 0.71 | 188 | -586 | -302 | 529 | 1022 | 0 | 0 | 0 | 0 | 0.1589 | 0.1317 | 831 | 109 | 61.9 | 33 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
2 | 2507 | 0.71 | 188 | -582 | -302 | 529 | 1022 | 0 | 0 | 0 | 0 | 0.1583 | 0.1312 | 831 | 109 | 61.9 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2507 | 0.71 | 188 | -582 | -307 | 528 | 1022 | 0 | 0 | 0 | 0 | 0.1583 | 0.1312 | 835 | 110 | 62.5 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
3 | 2508 | 0.71 | 188 | -582 | -307 | 528 | 1022 | 0 | 0 | 0 | 0 | 0.1583 | 0.1312 | 835 | 110 | 62.5 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2508 | 0.71 | 188 | -582 | -305 | 529 | 1022 | 0 | 0 | 0 | 0 | 0.1583 | 0.1312 | 834 | 109 | 61.9 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
4 | 2508 | 0.71 | 188 | -588 | -305 | 529 | 1022 | 0 | 0 | 0 | 0 | 0.1591 | 0.1318 | 834 | 110 | 62.5 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2507 | 0.71 | 188 | -588 | -306 | 529 | 1022 | 0 | 0 | 0 | 0 | 0.1591 | 0.1318 | 835 | 110 | 62.5 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
5 | 2508 | 0.71 | 188 | -588 | -306 | 530 | 1021 | 0 | 0 | 0 | 0 | 0.159 | 0.1319 | 836 | 110 | 62.5 | 32 | Fan Tests | Radial Swept | 22.1 | 50 | 12 | 0.075 | 0.0044 | 0.96
Data Series 7
0 | 2510 | 0.63 | 166 | -348 | -190 | 606 | 1021 | 0 | 0 | 0 | 0 | 0.1224 | 0.1015 | 796 | 81 | 52.6 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2509 | 0.63 | 166 | -348 | -190 | 606 | 1021 | 0 | 0 | 0 | 0 | 0.1224 | 0.1015 | 796 | 81 | 52.6 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
1 | 2509 | 0.62 | 164 | -348 | -190 | 605 | 1022 | 0 | 0 | 0 | 0 | 0.1224 | 0.1014 | 795 | 81 | 53.3 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2509 | 0.62 | 164 | -350 | -192 | 605 | 1022 | 0 | 0 | 0 | 0 | 0.1228 | 0.1018 | 797 | 81 | 53.3 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
2 | 2509 | 0.62 | 164 | -350 | -192 | 609 | 1021 | 0 | 0 | 0 | 0 | 0.1227 | 0.1018 | 801 | 82 | 53.9 | 29 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2510 | 0.61 | 161 | -354 | -193 | 609 | 1021 | 0 | 0 | 0 | 0 | 0.1234 | 0.1024 | 802 | 82 | 55 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
3 | 2510 | 0.61 | 161 | -354 | -193 | 607 | 1022 | 0 | 0 | 0 | 0 | 0.1235 | 0.1023 | 800 | 82 | 55 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2510 | 0.61 | 161 | -354 | -193 | 607 | 1022 | 0 | 0 | 0 | 0 | 0.1235 | 0.1023 | 800 | 82 | 55 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
4 | 2509 | 0.61 | 161 | -354 | -191 | 606 | 1022 | 0 | 0 | 0 | 0 | 0.1235 | 0.1023 | 797 | 82 | 55 | 30 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2509 | 0.6 | 159 | -344 | -191 | 606 | 1022 | 0 | 0 | 0 | 0 | 0.1217 | 0.1009 | 797 | 80 | 54.4 | 29 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
5 | 2509 | 0.61 | 161 | -344 | -192 | 608 | 1022 | 0 | 0 | 0 | 0 | 0.1217 | 0.1009 | 800 | 81 | 54.4 | 29 | Fan Tests | Radial Swept | 22.1 | 40 | 12 | 0.075 | 0.0044 | 0.96
Data Series 8
0 | 2509 | 0.57 | 149 | -220 | -112 | 644 | 1022 | 0 | 0 | 0 | 0 | 0.0973 | 0.0806 | 756 | 61 | 44.5 | 27 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2511 | 0.54 | 142 | -186 | -112 | 644 | 1021 | 0 | 0 | 0 | 0 | 0.0895 | 0.0742 | 756 | 56 | 43.1 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
1 | 2510 | 0.54 | 142 | -186 | -110 | 643 | 1021 | 0 | 0 | 0 | 0 | 0.0895 | 0.0742 | 753 | 56 | 43.1 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2511 | 0.53 | 140 | -186 | -110 | 643 | 1022 | 0 | 0 | 0 | 0 | 0.0895 | 0.0742 | 753 | 56 | 43.8 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
2 | 2510 | 0.52 | 137 | -186 | -108 | 646 | 1022 | 0 | 0 | 0 | 0 | 0.0895 | 0.0742 | 754 | 56 | 44.8 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2510 | 0.51 | 135 | -186 | -108 | 646 | 1022 | 0 | 0 | 0 | 0 | 0.0895 | 0.0742 | 754 | 56 | 45.5 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
3 | 2511 | 0.51 | 135 | -186 | -110 | 646 | 1022 | 0 | 0 | 0 | 0 | 0.0895 | 0.0742 | 756 | 56 | 45.5 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2511 | 0.51 | 135 | -186 | -110 | 646 | 1021 | 0 | 0 | 0 | 0 | 0.0895 | 0.0742 | 756 | 56 | 45.5 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
4 | 2511 | 0.51 | 135 | -186 | -110 | 646 | 1021 | 0 | 0 | 0 | 0 | 0.0895 | 0.0742 | 756 | 56 | 45.5 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2510 | 0.51 | 135 | -186 | -110 | 647 | 1022 | 0 | 0 | 0 | 0 | 0.0895 | 0.0742 | 757 | 56 | 45.5 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
5 | 2512 | 0.51 | 135 | -190 | -108 | 647 | 1022 | 0 | 0 | 0 | 0 | 0.0905 | 0.075 | 755 | 57 | 46.3 | 26 | Fan Tests | Radial Swept | 22.1 | 30 | 12 | 0.075 | 0.0044 | 0.96
Data Series 9
0 | 2511 | 0.46 | 123 | -96 | -57 | 669 | 1022 | 0 | 0 | 0 | 0 | 0.0643 | 0.0533 | 726 | 39 | 35.1 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2512 | 0.45 | 120 | -96 | -57 | 666 | 1022 | 0 | 0 | 0 | 0 | 0.0643 | 0.0533 | 723 | 39 | 36.1 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
1 | 2511 | 0.45 | 120 | -96 | -57 | 666 | 1022 | 0 | 0 | 0 | 0 | 0.0643 | 0.0533 | 723 | 39 | 36.1 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2512 | 0.45 | 120 | -96 | -57 | 666 | 1022 | 0 | 0 | 0 | 0 | 0.0643 | 0.0533 | 723 | 39 | 36.1 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
2 | 2511 | 0.45 | 118 | -96 | -57 | 666 | 1021 | 0 | 0 | 0 | 0 | 0.0643 | 0.0533 | 723 | 39 | 36.8 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2511 | 0.45 | 118 | -96 | -58 | 666 | 1021 | 0 | 0 | 0 | 0 | 0.0643 | 0.0533 | 724 | 39 | 36.8 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
3 | 2512 | 0.45 | 118 | -96 | -58 | 669 | 1021 | 0 | 0 | 0 | 0 | 0.0643 | 0.0533 | 727 | 39 | 36.8 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2512 | 0.45 | 118 | -98 | -58 | 669 | 1021 | 0 | 0 | 0 | 0 | 0.0649 | 0.0538 | 727 | 39 | 36.8 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
4 | 2513 | 0.45 | 118 | -98 | -58 | 668 | 1022 | 0 | 0 | 0 | 0 | 0.065 | 0.0539 | 726 | 39 | 36.8 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2512 | 0.45 | 118 | -94 | -58 | 668 | 1022 | 0 | 0 | 0 | 0 | 0.0636 | 0.0527 | 726 | 38 | 35.8 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
5 | 2513 | 0.45 | 118 | -94 | -58 | 668 | 1022 | 0 | 0 | 0 | 0 | 0.0636 | 0.0527 | 726 | 38 | 35.8 | 23 | Fan Tests | Radial Swept | 22.1 | 20 | 12 | 0.075 | 0.0044 | 0.96
Data Series 10
0 | 2512 | 0.39 | 104 | -24 | 3 | 688 | 1022 | 0 | 0 | 0 | 0 | 0.0321 | 0.0266 | 685 | 18 | 19.6 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2513 | 0.39 | 104 | -24 | -6 | 682 | 1022 | 0 | 0 | 0 | 0 | 0.0321 | 0.0266 | 688 | 18 | 19.6 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
1 | 2513 | 0.39 | 104 | -26 | -6 | 682 | 1022 | 0 | 0 | 0 | 0 | 0.0335 | 0.0278 | 688 | 19 | 20.7 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2513 | 0.38 | 101 | -26 | -4 | 686 | 1022 | 0 | 0 | 0 | 0 | 0.0335 | 0.0278 | 690 | 19 | 21.3 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
2 | 2514 | 0.38 | 101 | -26 | -4 | 686 | 1021 | 0 | 0 | 0 | 0 | 0.0334 | 0.0277 | 690 | 19 | 21.3 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2513 | 0.38 | 101 | -24 | -5 | 686 | 1021 | 0 | 0 | 0 | 0 | 0.0321 | 0.0266 | 691 | 18 | 20.2 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
3 | 2513 | 0.38 | 101 | -24 | -5 | 685 | 1022 | 0 | 0 | 0 | 0 | 0.0321 | 0.0266 | 690 | 18 | 20.2 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2512 | 0.38 | 101 | -26 | -4 | 685 | 1022 | 0 | 0 | 0 | 0 | 0.0335 | 0.0278 | 689 | 19 | 21.3 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
4 | 2512 | 0.38 | 101 | -26 | -4 | 684 | 1022 | 0 | 0 | 0 | 0 | 0.0335 | 0.0278 | 688 | 19 | 21.3 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2512 | 0.38 | 101 | -24 | -4 | 684 | 1022 | 0 | 0 | 0 | 0 | 0.0321 | 0.0266 | 688 | 18 | 20.2 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
5 | 2513 | 0.38 | 101 | -24 | -6 | 690 | 1022 | 0 | 0 | 0 | 0 | 0.0321 | 0.0266 | 696 | 19 | 21.3 | 17 | Fan Tests | Radial Swept | 22.1 | 10 | 12 | 0.075 | 0.0044 | 0.96
Data Series 11
0 | 2513 | 0.35 | 94 | 0 | 36 | 714 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 678 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96
0.5 | 2513 | 0.35 | 94 | 0 | 38 | 714 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 676 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96
1 | 2514 | 0.34 | 92 | 0 | 38 | 714 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 676 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96
1.5 | 2513 | 0.34 | 91 | 0 | 36 | 714 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 678 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96
2 | 2513 | 0.34 | 91 | 0 | 36 | 711 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 675 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96
2.5 | 2513 | 0.34 | 89 | 0 | 39 | 711 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 672 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96
3 | 2513 | 0.34 | 91 | 0 | 39 | 712 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 673 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96
3.5 | 2513 | 0.34 | 89 | 0 | 39 | 712 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 673 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96
4 | 2513 | 0.34 | 89 | 0 | 39 | 707 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 668 | 0 | 0 | 0 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96
4.5 | 2514 | 0.34 | 89 | -2 | 39 | 707 | 1022 | 0 | 0 | 0 | 0 | 0.0093 | 0.0077 | 668 | 5 | 6.5 | 9 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96
5 | 2513 | 0.34 | 89 | -2 | 39 | 714 | 1022 | 0 | 0 | 0 | 0 | 0.0093 | 0.0077 | 675 | 5 | 6.5 | 9 | Fan Tests | Radial Swept | 22.1 | 0 | 12 | 0.075 | 0.0044 | 0.96